## BESS_technical
BESS_sim.py version 2022.12.20
BESS technical parameters | BESS_1 | BESS_2 | Unit | Comments
Rated active power for up-reg. | 80 | 60 | MW | output to the grid or discharge
Rated active power for down-reg. | 80 | 60 | MW | input from the grid or charge
Rated energy capacity (discharge = to the grid) | 160 | 120 | MWh
Min SOC limit / permitted DOD | 10 | 10 | %
Max SOC limit / permitted DOC | 90 | 90 | %
Charging efficiency | 0.95 | 0.95 | [0–1] | including all components (i.e. [Energy into battery] / [Energy from grid])
Discharging efficiency | 0.95 | 0.95 | [0–1] | including all components (i.e. [Energy to grid] / [Energy from battery])
Round-trip efficiency (AC/AC) |  |  | [0–1] | including all components (i.e. [Energy to grid] / [Energy from grid])
Self-discharge | 0.08 | 0.08 | %/day | losses not included in efficiency, occurring regardless of BESS being idle or active, expressed as % of SOC per day
Min cycling per 24 hours |  |  | cycle/day | minimum amount of energy to be discharged within any 24-h period, 1 cycle = sum discharge equal to rated capacity
Ensure min cycling? | no |  |  | if no, only reports if min cycling has failed to occur; if yes, attempts BESS_1 <-> BESS_2 cycling for min condition
[6 empty] | SOC0 | SOC0 | init_unit
BESS simulation settings | BESS_1 | BESS_2 |  |  |  | BESS1 | BESS2 | BESS1 | BESS2
Initial state of charge | 50 | 50 | % |  | min | 16 | 12 | 10 | 10
Storage qualified as LER | yes | yes |  | Limited energy reservoir | max | 144 | 108 | 90 | 90
BESS availability | yes | no |  | Select "no" if the specific BESS is to be considered unavailable during the simulation
LER SOC management strategy | Active | Conservative |  | Conservative strategy: to fulfill minimum LER requirements; Active strategy: manage SOC like a non-LER resource
Simulation time resolution | 1 |  | min
Intraday bid acceptance probability | 100 |  | %
Frequency input file | FI_2022_scenario_frequency.csv |  |  | Specify the csv, xls or xlsx input file name.
FRR activation input file | FI_2022_scenario_FRR.csv
Scenario name for result output | FI Active |  |  | Specify the name for the result output files.
BESS reserve provision settings | BESS_1 | BESS_2 | BESS fleet | Reserve provision to be defined for the BESS fleet or BESS 1&2 separately. The cells in red should not be left blank
Uniform mandatory FCR capacity during the day | yes | yes | n/a | If no selected, provide variable FCR capacity bids for each MTU in the sheet BESS_capacity_bids
Uniform mandatory FRR capacity during the day | yes | yes | n/a | If no selected, provide variable FRR UP and DOWN capacity bids for each MTU in the sheet BESS_capacity_bids
Uniform mandatory FCR capacity, MW | 8 | 6 | 8 | For a uniform FCR, provide the capacity for the whole simulation period
Mandatory FRR UP capacity, MW | 32 | 24 | 32 | For a uniform FRR, provide the UP capacity for the whole period
Mandatory FRR DOWN capacity, MW | 32 | 24 | 32 | For a uniform FRR, provide the DOWN capacity for the whole period
Allow voluntary FRR energy bids? | no | no | n/a | Select n/a for BESS 1&2 if reserve provision has been defined for the BESS fleet, and vice versa
Reserve market and user settings
Capacity market GCT:
FCR | 7:30 | @ hh:mm | day before
FRR | 9:00
Energy market GCT:
FRR | 25 | minutes before MTU
Intraday | 60
User decision time for bids:
FCR capacity | 5 | minutes before GCT
FRR capacity | 5
FRR energy | 5 | minutes before GCT
Intraday | 5
Power system frequency settings:
Target frequency | 50 | Hz
FCR full activation @ Δf = | 0.2 | Hz
Frequency deadband for FCR activation | 0.01 | Hz
Minimum duration of full FCR activation by LER | 30 | min |  | tminLER
aFRR full activation time | 5 | min |  | Duration of LER transition to reserve mode when providing FCR if the energy reservoir depleted
LER max recovery time | 2 | h |  | Time limit for recovering full FCR capabilities after Alert State (in which tminLER was met)
Note on C38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: D-1 7:30 - GCT D-1 8:00 - Results
Note on C39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: D-1 9:00 - GCT D-1 10:00 - Results

## BESS_capacity_bids
|  | capacity (MW) per MTU |  |  | capacity (MW) per MTU
Market time unit
MTU 1 00:00–00:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 2 00:15–00:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 3 00:30–00:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 4 00:45–01:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 5 01:00–01:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 6 01:15–01:30 | 0 | 12 | 8 | 3 | 27 | 30
MTU 7 01:30–01:45 | 0 | 12 | 8 | 3 | 27 | 30
MTU 8 01:45–02:00 | 0 | 12 | 8 | 3 | 27 | 30
MTU 9 02:00–02:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 10 02:15–02:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 11 02:30–02:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 12 02:45–03:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 13 03:00–03:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 14 03:15–03:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 15 03:30–03:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 16 03:45–04:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 17 04:00–04:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 18 04:15–04:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 19 04:30–04:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 20 04:45–05:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 21 05:00–05:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 22 05:15–05:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 23 05:30–05:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 24 05:45–06:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 25 06:00–06:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 26 06:15–06:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 27 06:30–06:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 28 06:45–07:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 29 07:00–07:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 30 07:15–07:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 31 07:30–07:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 32 07:45–08:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 33 08:00–08:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 34 08:15–08:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 35 08:30–08:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 36 08:45–09:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 37 09:00–09:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 38 09:15–09:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 39 09:30–09:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 40 09:45–10:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 41 10:00–10:15 | 8 | 12 | 8 | 3 | 27 | 30
MTU 42 10:15–10:30 | 8 | 12 | 8 | 3 | 27 | 30
MTU 43 10:30–10:45 | 8 | 12 | 8 | 3 | 27 | 30
MTU 44 10:45–11:00 | 8 | 12 | 8 | 3 | 27 | 30
MTU 45 11:00–11:15 | 10 | 12 | 8 | 3 | 27 | 20
MTU 46 11:15–11:30 | 10 | 12 | 8 | 3 | 27 | 20
MTU 47 11:30–11:45 | 10 | 12 | 8 | 3 | 27 | 20
MTU 48 11:45–12:00 | 10 | 12 | 8 | 3 | 27 | 20
MTU 49 12:00–12:15 | 10 | 12 | 8 | 3 | 27 | 20
MTU 50 12:15–12:30 | 10 | 12 | 8 | 3 | 27 | 20
MTU 51 12:30–12:45 | 10 | 12 | 8 | 3 | 27 | 20
MTU 52 12:45–13:00 | 10 | 12 | 8 | 3 | 27 | 20
MTU 53 13:00–13:15 | 10 | 12 | 8 | 3 | 27 | 20
MTU 54 13:15–13:30 | 10 | 12 | 8 | 3 | 27 | 20
MTU 55 13:30–13:45 | 10 | 12 | 8 | 3 | 27 | 20
MTU 56 13:45–14:00 | 10 | 12 | 8 | 3 | 27 | 20
MTU 57 14:00–14:15 | 10 | 20 | 8 | 7 | 23 | 20
MTU 58 14:15–14:30 | 10 | 20 | 8 | 7 | 23 | 20
MTU 59 14:30–14:45 | 10 | 20 | 8 | 7 | 23 | 20
MTU 60 14:45–15:00 | 10 | 20 | 8 | 7 | 23 | 20
MTU 61 15:00–15:15 | 10 | 20 | 8 | 7 | 23 | 20
MTU 62 15:15–15:30 | 10 | 20 | 8 | 7 | 23 | 20
MTU 63 15:30–15:45 | 10 | 20 | 8 | 7 | 23 | 20
MTU 64 15:45–16:00 | 10 | 20 | 8 | 7 | 23 | 20
MTU 65 16:00–16:15 | 10 | 20 | 8 | 7 | 23 | 20
MTU 66 16:15–16:30 | 10 | 20 | 8 | 7 | 23 | 20
MTU 67 16:30–16:45 | 10 | 20 | 8 | 7 | 23 | 20
MTU 68 16:45–17:00 | 10 | 20 | 8 | 7 | 23 | 20
MTU 69 17:00–17:15 | 10 | 20 | 8 | 7 | 23 | 20
MTU 70 17:15–17:30 | 10 | 20 | 8 | 7 | 23 | 20
MTU 71 17:30–17:45 | 10 | 20 | 8 | 7 | 23 | 20
MTU 72 17:45–18:00 | 10 | 20 | 8 | 7 | 23 | 20
MTU 73 18:00–18:15 | 4 | 20 | 0 | 7 | 23 | 20
MTU 74 18:15–18:30 | 4 | 20 | 0 | 7 | 23 | 20
MTU 75 18:30–18:45 | 4 | 20 | 0 | 7 | 23 | 20
MTU 76 18:45–19:00 | 4 | 20 | 0 | 7 | 23 | 20
MTU 77 19:00–19:15 | 4 | 8 | 0 | 7 | 23 | 20
MTU 78 19:15–19:30 | 4 | 8 | 0 | 7 | 23 | 20
MTU 79 19:30–19:45 | 4 | 8 | 0 | 7 | 23 | 20
MTU 80 19:45–20:00 | 4 | 8 | 0 | 7 | 23 | 20
MTU 81 20:00–20:15 | 4 | 8 | 0 | 7 | 23 | 20
MTU 82 20:15–20:30 | 4 | 8 | 0 | 7 | 23 | 20
MTU 83 20:30–20:45 | 4 | 8 | 0 | 7 | 23 | 20
MTU 84 20:45–21:00 | 4 | 8 | 0 | 7 | 23 | 20
MTU 85 21:00–21:15 | 4 | 8 | 0 | 7 | 23 | 20
MTU 86 21:15–21:30 | 4 | 8 | 0 | 7 | 23 | 20
MTU 87 21:30–21:45 | 4 | 8 | 0 | 7 | 23 | 20
MTU 88 21:45–22:00 | 4 | 8 | 0 | 7 | 23 | 20
MTU 89 22:00–22:15 | 4 | 8 | 0 | 10 | 20 | 20
MTU 90 22:15–22:30 | 4 | 8 | 0 | 10 | 20 | 20
MTU 91 22:30–22:45 | 4 | 8 | 0 | 10 | 20 | 20
MTU 92 22:45–23:00 | 4 | 8 | 0 | 10 | 20 | 20
MTU 93 23:00–23:15 | 4 | 8 | 8 | 10 | 20 | 20
MTU 94 23:15–23:30 | 4 | 8 | 8 | 10 | 20 | 20
MTU 95 23:30–23:45 | 4 | 8 | 8 | 10 | 20 | 20
MTU 96 23:45–00:00 | 4 | 8 | 8 | 10 | 20 | 20

## List (hidden)
BESS_1 | BESS_2 | or BESS fleet
yes | yes | n/a | If "no", provide variable FCR capacity bids for each MTU. | TRUE
yes | no | n/a
no | yes | n/a
no | no | n/a
n/a | n/a | yes
n/a | n/a | no
Note on D3: Kārlis Baltputnis: TODO: make Excel rule to disallow input in 'BESS-1' and 'BESS-2', if 'fleet' has value.